## UTILRNWL
| Life | Length | Number | Average | Replacement | Total | Avg | Sum of | 1990
Utility Type | Expect. | in feet | of | Size | Unit Cost | Replacement | Age | Digits in | Renewal
| in years |  | Items |  |  | Cost |  | Life Expect. | Allowance
[11 empty] | LOOKUP TABLE |  | LOOKUP TABLE -LIFE EXPECTANCY
DELGADO COMMUNITY COLLEGE | [14 empty] | {/ Publish;ShadingGrey}
{RIGHT 9}~
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0 | \-~ | 0 | 0 | Concrete Roads & Streets | 40
Asphalt Roads & Streets | 20 | 0 |  |  |  | 0 |  | 210 | 0 | {DOWN}@SUM({UP}{END}{UP}.{END}{DOWN})~ | 1 | 1 | Asphalt Roads & Streets | 20
Water | 60 | 6371 |  | 5 | 55 | 350405 | 25 | 1830 | 4786.9536 |  | 2 | 3 | Water | 60
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0 |  | 3 | 6 | Fire Mains w/Hydrants | 60
Fire Hydrants on Domestic Main | 60 |  | 12 |  | 1200 | 14400 | 25 | 1830 | 196.7213 |  | 4 | 10 | Fire Hydrants on Domestic Main | 60
Sanitary Sewer | 60 | 6850 |  | 6 | 90 | 616500 | 25 | 1830 | 8422.1311 |  | 5 | 15 | Sanitary Sewer | 60
Storm Sewer | 40 | 8020 |  | 12 | 80 | 641600 | 25 | 820 | 19560.9756 |  | 6 | 21 | Storm Sewer | 40
Gas | 30 | 3770 |  | 2 | 80 | 301600 | 25 | 465 | 16215.0538 |  | 7 | 28 | Gas | 30
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0 |  | 8 | 36 | Steam & Condensate | 35
Hot Water | 40 | 1400 |  | 5 | 125 | 175000 | 25 | 820 | 5335.3659 |  | 9 | 45 | Hot Water | 40
Chilled Water | 40 | 1400 |  | 8 | 180 | 252000 | 25 | 820 | 7682.9268 |  | 10 | 55 | Chilled Water | 40
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0 |  | 11 | 66 | Domestic Hot Water | 40
Compressed Air | 40 | 1400 |  | 0.375 | 20 | 28000 | 25 | 820 | 853.6585 |  | 12 | 78 | Compressed Air | 40
Electrical - Underground | 30 | 8700 |  |  | 90 | 783000 | 25 | 465 | 42096.7742 |  | 13 | 91 | Electrical - Underground | 30
Electrical - Overhead | 50 | [6 empty] | 1275 | 0 |  | 14 | 105 | Street Lights - Elec UG | 30
Street Lights - Elec UG | 30 | 7000 |  |  | 45 | 315000 | 25 | 465 | 16935.4839 |  | 15 | 120 | Street Light Standards | 60
Street Light Standards | 60 |  | 76 |  | 2000 | 152000 | 25 | 1830 | 2076.5027 |  | 16 | 136 | Fire Hydrants | 60
Water Wells | 25 | 0 |  |  |  | 0 |  | 325 | 0 |  | 17 | 153 | Water Wells | 25
Internet Connectivity Network | 25 | [6 empty] | 325
Emergency Alert System | 25 | [6 empty] | 325
Parking Lots Concrete (in acres) | 25 | [6 empty] | 325
Parking Lots Asphalt (in acres) | 25 | [6 empty] | 325
Parking Lots Gravel/Shell (in acres) | 25 | [6 empty] | 325
[11 empty] | 18 | 171 | Fences | 30
Total | [5 empty] | 3629505 |  |  | 124162.5474 |  | 19 | 190 | Sewage Treatment Plants | 20
[11 empty] | 20 | 210 | Gravel Roads | 10
¦:: | [10 empty] | 21 | 231 | Drainage Structures | 20
GRAMBLING STATE UNIVERSITY | [10 empty] | 22 | 253 | Shell Paving | 5
[11 empty] | 23 | 276 | Aquaculture Ponds | 10
Concrete Roads & Streets | 40 | 2093 |  | 22 | 65 | 136045 | 18 | 820 | 2986.3537 |  | 24 | 300 | Electrical - Overhead | 50
Asphalt Roads & Streets | 20 | 22125 |  | 30 | 59 | 1305375 | 20 | 210 | 124321.4286 |  | 25 | 325
Water | 60 | 37086 |  | 4 | 55 | 2039730 | 15 | 1830 | 16719.0984 |  | 26 | 351
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0 |  | 27 | 378
Fire Hydrants on Domestic Main | 60 |  | 44 |  | 1200 | 52800 | 10 | 1830 | 288.5246 |  | 28 | 406
Sanitary Sewer | 60 | 12678 |  | 8 | 100 | 1267800 | 10 | 1830 | 6927.8689 |  | 29 | 435
Storm Sewer | 40 | 10270 |  | 48 | 210 | 2156700 | 10 | 820 | 26301.2195 |  | 30 | 465
Gas | 30 | 23780 |  | 2 | 80 | 1902400 | 12 | 465 | 49094.1935 |  | 31 | 496
Steam & Condensate | 35 | 1200 |  | 2 | 130 | 156000 | 28 | 630 | 6933.3333 |  | 32 | 528
Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0 |  | 33 | 561
Chilled Water | 40 | 400 |  | 4 | 160 | 64000 | 16 | 820 | 1248.7805 |  | 34 | 595
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0 |  | 35 | 630
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0 |  | 36 | 666
Electrical - Underground | 30 | 14798 |  |  | 90 | 1331820 | 25 | 465 | 71603.2258 |  | 37 | 703
Electrical - Overhead | 50 | 15361 |  |  | 6.5 | 99846.5 | 20 | 1275 | 1566.2196 |  | 38 | 741
Street Lights - Elec UG | 30 | 26040 |  |  | 45 | 1171800 | 15 | 465 | 37800 |  | 39 | 780
Street Light Standards | 60 |  | 223 |  | 2000 | 446000 | 10 | 1830 | 2437.1585 |  | 40 | 820
Water Wells | 25 |  |  |  |  | 115000 | 8 | 325 | 2830.7692 |  | 41 | 861
Aerated Sewage Lagoon | 10 |  |  |  |  | 169000 | 3 | 55 | 9218.1818 |  | 42 | 903
Water Tower #1 100,000gal | 60 |  |  |  |  | 125000 | 40 | 1830 | 2732.2404 |  | 43 | 946
Water Tower #2 200,000gal | 60 |  |  |  |  | 219000 | 11 | 1830 | 1316.3934 |  | 44 | 990
Radio Trans Tower 460' | 60 |  |  |  |  | 60000 | 1 | 1830 | 32.7869 |  | 45 | 1035
High Mast Light Towers | 50 |  | 2 |  | 25000 | 50000 | 7 | 1275 | 274.5098 |  | 46 | 1081
[11 empty] | 47 | 1128
Total | [5 empty] | 12868316.5 |  |  | 364632.2864 |  | 48 | 1176
[11 empty] | 49 | 1225
¦:: | [10 empty] | 50 | 1275
[11 empty] | 51 | 1326
LOUISIANA TECH UNIVERSITY | [10 empty] | 52 | 1378
[11 empty] | 53 | 1431
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0 |  | 54 | 1485
Asphalt Roads & Streets | 20 | 18500 |  | 26 | 53 | 980500 | 35 | 210 | 163416.6667 |  | 55 | 1540
Water | 60 | 47700 |  | 4 | 55 | 2623500 | 30 | 1830 | 43008.1967 |  | 56 | 1596
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0 |  | 57 | 1653
Fire Hydrants on Domestic Main | 60 |  | 32 |  | 1200 | 38400 | 30 | 1830 | 629.5082 |  | 58 | 1711
Sanitary Sewer | 60 | 19657 |  | 6 | 90 | 1769130 | 25 | 1830 | 24168.4426 |  | 59 | 1770
Storm Sewer | 40 | 12500 |  | 15 | 95 | 1187500 | 25 | 820 | 36204.2683 |  | 60 | 1830
Gas | 30 | 7320 |  | 1.5 | 75 | 549000 | 25 | 465 | 29516.129
Steam & Condensate | 35 | 22500 |  | 8 | 150 | 3375000 | 30 | 630 | 160714.2857
Hot Water | 40 | 390 |  | 6 | 130 | 50700 | 15 | 820 | 927.439
Chilled Water | 40 | 390 |  | 6 | 170 | 66300 | 15 | 820 | 1212.8049
Domestic Hot Water | 40 | 390 |  | 2 | 70 | 27300 | 25 | 820 | 832.3171
Compressed Air | 40 | 200 |  | 2 | 40 | 8000 | 25 | 820 | 243.9024
Electrical - Underground | 30 | 46500 |  |  | 90 | 4185000 | 20 | 465 | 180000
Electrical - Overhead | 50 | 0 | [5 empty] | 1275 | 0
Street Lights - Elec UG | 30 | 4500 |  |  | 45 | 202500 | 15 | 465 | 6532.2581
Street Light Standards | 60 |  | 147 |  | 2000 | 294000 | 15 | 1830 | 2409.8361
Water Wells | 25 |  |  |  |  | 300000 | 20 | 325 | 18461.5385
Water Tower 125,000 gal | 60 |  |  |  |  | 155000 | 50 | 1830 | 4234.9727
High Mast Light Towers | 50 |  | 14 |  | 25000 | 350000 | 7 | 1275 | 1921.5686
Total | [5 empty] | 16161830 |  |  | 674434.1346
¦::
MCNEESE STATE UNIVERSITY
Concrete Roads & Streets | 40 | 8720 |  | 24 | 70 | 610400 | 40 | 820 | 29775.6098
Asphalt Roads & Streets | 20 | 5890 |  | 24 | 50 | 294500 | 40 | 210 | 56095.2381
Water | 60 | 13485 |  | 4 | 55 | 741675 | 40 | 1830 | 16211.4754
Fire Mains w/Hydrants | 60 | 5460 |  | 12 | 110 | 600600 | 25 | 1830 | 8204.918
Fire Hydrants on Domestic Main | 60 | [6 empty] | 1830 | 0
Sanitary Sewer | 60 | 10007 |  | 6 | 90 | 900630 | 35 | 1830 | 17225.1639
Storm Sewer | 40 | 10028 |  | 18 | 110 | 1103080 | 40 | 820 | 53808.7805
Gas | 30 | 14715 |  | 2 | 80 | 1177200 | 35 | 465 | 88606.4516
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 13200 |  | 6 | 130 | 1716000 | 6 | 820 | 12556.0976
Chilled Water | 40 | 13200 |  | 8 | 180 | 2376000 | 6 | 820 | 17385.3659
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 13240 |  |  | 90 | 1191600 | 12 | 465 | 30750.9677
Electrical - Overhead | 50 | 0 |  |  |  | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 10000 |  |  | 45 | 450000 | 25 | 465 | 24193.5484
Street Light Standards | 60 |  | 57 |  | 2000 | 114000 | 25 | 1830 | 1557.377
Water Wells | 25 |  |  |  |  | 87000 | 30 | 325 | 8030.7692
Total | [5 empty] | 11362685 |  |  | 364401.7632
¦::
NICHOLLS STATE UNIVERSITY
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 | 21 | 820 | 0
Asphalt Roads & Streets | 20 | 0 |  |  |  | 0 | 21 | 210 | 0
Water | 60 | 2000 |  | 1 | 40 | 80000 | 21 | 1830 | 918.0328
Fire Mains w/Hydrants | 60 | 100 |  | 6 | 75 | 7500 | 21 | 1830 | 86.0656
Fire Hydrants on Domestic Main | 60 |  | 0 |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 2500 |  | 6 | 90 | 225000 | 21 | 1830 | 2581.9672
Storm Sewer | 40 | 4000 |  | 12 | 80 | 320000 | 21 | 820 | 8195.122
Gas | 30 | 500 |  | 1 | 75 | 37500 | 21 | 465 | 1693.5484
Steam & Condensate | 35 | 0 |  |  |  | 0 | 21 | 630 | 0
Hot Water | 40 | 400 |  | 4 | 120 | 48000 | 21 | 820 | 1229.2683
Chilled Water | 40 | 400 |  | 4 | 160 | 64000 | 21 | 820 | 1639.0244
Domestic Hot Water | 40 | 0 |  |  |  | 0 | 21 | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 | 21 | 820 | 0
Electrical - Underground | 30 | 15000 |  |  | 90 | 1350000 | 21 | 465 | 60967.7419
Electrical - Overhead | 50 | 0 |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 0 |  |  | 45 | 0 | 21 | 465 | 0
Street Light Standards | 60 |  | 0 |  | 2000 | 0 |  | 1830 | 0
Water Wells | 25 | 0 |  |  |  | 0 |  | 325 | 0
Total | [5 empty] | 2132000 |  |  | 77310.7705
¦::
NORTHEAST LOUISIANA UNIVERSITY
Concrete Roads & Streets | 40 | 11610 |  | 32 | 90 | 1044900 | 20 | 820 | 25485.3659
Asphalt Roads & Streets | 20 | 2000 |  | 32 | 62 | 124000 | 25 | 210 | 14761.9048
Water | 60 | 11585 |  | 1.5 | 42.5 | 492362.5 | 20 | 1830 | 5381.0109
Fire Mains w/Hydrants | 60 | 600 |  | 4 | 70 | 42000 | 20 | 1830 | 459.0164
Fire Hydrants on Domestic Main | 60 |  |  |  | 1200 | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 21390 |  | 6 | 90 | 1925100 | 20 | 1830 | 21039.3443
Storm Sewer | 40 | 27220 |  | 18 | 110 | 2994200 | 20 | 820 | 73029.2683
Gas | 30 | 27668 |  | 2.4 | 82.5 | 2282610 | 15 | 465 | 73632.5806
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 | 1995 |  | 4 | 160 | 319200 | 20 | 820 | 7785.3659
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 12565 |  |  | 90 | 1130850 | 25 | 465 | 60798.3871
Electrical - Overhead | 50 |  |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 38830 |  |  | 45 | 1747350 | 25 | 465 | 93943.5484
Street Light Standards | 60 |  | 297 |  | 2000 | 594000 | 25 | 1830 | 8114.7541
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Total | [5 empty] | 12696572.5 |  |  | 384430.5466
¦::
NORTHWESTERN STATE UNIVERSITY
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 42240 |  | 18.5 | 42 | 1774080 | 12.5 | 210 | 105600
Water | 60 | 59350 |  | 8 | 60 | 3561000 | 12 | 1830 | 23350.8197
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0
Fire Hydrants on Domestic Main | 60 |  | 39 |  | 1200 | 46800 | 12 | 1830 | 306.8852
Sanitary Sewer | 60 | 25000 |  | 8 | 100 | 2500000 | 10 | 1830 | 13661.2022
Storm Sewer | 40 | 15500 |  | 24 | 135 | 2092500 | 30 | 820 | 76554.878
Gas | 30 | 0 |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 | 20000 |  | 5 | 150 | 3000000 | 9 | 630 | 42857.1429
Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 | 16500 |  | 10 | 185 | 3052500 | 20 | 820 | 74451.2195
Domestic Hot Water | 40 | 1776 |  | 1.5 | 65 | 115440 | 24 | 820 | 3378.7317
Compressed Air | 40 | 16500 |  | 0.5 | 25 | 412500 | 20 | 820 | 10060.9756
Electrical - Underground | 30 | 32000 |  |  | 90 | 2880000 | 10 | 465 | 61935.4839
Electrical - Overhead | 50 | 0 |  |  |  | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 56000 |  |  | 45 | 2520000 | 10 | 465 | 54193.5484
Street Light Standards | 60 |  | 340 |  | 2000 | 680000 | 10 | 1830 | 3715.847
Water Wells | 25 |  |  |  |  | 50000 | 16 | 325 | 2461.5385
Total | [5 empty] | 22684820 |  |  | 472528.2726
¦::
SOUTHEASTERN LOUISIANA UNIVERSITY
Concrete Roads & Streets | 40 | 3100 |  | 24 | 70 | 217000 | 30 | 820 | 7939.0244
Asphalt Roads & Streets | 20 | 26300 |  | 24 | 50 | 1315000 | 30 | 210 | 187857.1429
Water | 60 | 24288 |  | 6 | 60 | 1457280 | 30 | 1830 | 23889.8361
Fire Mains w/Hydrants | 60 | 12000 |  | 6 | 75 | 900000 | 25 | 1830 | 12295.082
Fire Hydrants on Domestic Main | 60 |  |  |  | 1200 | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 28512 |  | 4 | 85 | 2423520 | 30 | 1830 | 39729.8361
Storm Sewer | 40 | 27456 |  | 12 | 80 | 2196480 | 25 | 820 | 66965.8537
Gas | 30 | 22176 |  | 1.5 | 75 | 1663200 | 25 | 465 | 89419.3548
Steam & Condensate | 35 | 300 |  | 2 | 130 | 39000 | 35 | 630 | 2166.6667
Hot Water | 40 | 2314 |  | 4 | 120 | 277680 | 12 | 820 | 4063.6098
Chilled Water | 40 | 2314 |  | 4 | 160 | 370240 | 12 | 820 | 5418.1463
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 33714 |  |  | 90 | 3034260 | 17 | 465 | 110929.9355
Street Lights - Elec UG | 30 | 38175 |  |  | 45 | 1717875 | 15 | 465 | 55415.3226
Street Light Standards | 60 |  | 197 |  | 2000 | 394000 | 15 | 1830 | 3229.5082
Water Wells | 25 |  |  |  |  | 13000 | 35 | 325 | 1400
Underground Tanks | 25 |  |  |  |  | 75000 | 10 | 325 | 2307.6923
Total | [5 empty] | 16093535 |  |  | 613027.0112
¦::
UNIVERSITY OF SOUTHWESTERN LOUISIANA
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 15000 |  | 20 | 44 | 660000 | 20 | 210 | 62857.1429
Water | 60 | 28000 |  | 3 | 50 | 1400000 | 40 | 1830 | 30601.0929
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0
Fire Hydrants on Domestic Main | 60 |  | 20 |  | 1200 | 24000 | 40 | 1830 | 524.5902
Sanitary Sewer | 60 | 36000 |  | 8 | 100 | 3600000 | 40 | 1830 | 78688.5246
Storm Sewer | 40 | 15000 |  | 36 | 180 | 2700000 | 40 | 820 | 131707.3171
Gas | 30 | 12000 |  | 2 | 80 | 960000 | 20 | 465 | 41290.3226
Steam & Condensate | 35 | 400 |  | 2 | 130 | 52000 | 40 | 630 | 3301.5873
Hot Water | 40 | 2200 |  | 6 | 130 | 286000 | 20 | 820 | 6975.6098
Chilled Water | 40 | 8000 |  | 6 | 170 | 1360000 | 20 | 820 | 33170.7317
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 2700 |  | 0.5 | 25 | 67500 | 20 | 820 | 1646.3415
Electrical - Underground | 30 | 36000 |  |  | 90 | 3240000 | 30 | 465 | 209032.2581
Street Lights - Elec UG | 30 | 30000 |  |  | 45 | 1350000 | 20 | 465 | 58064.5161
Street Light Standards | 60 |  | 265 |  | 2000 | 530000 | 20 | 1830 | 5792.3497
Water Wells | 25 |  |  |  |  | 60000 | 10 | 325 | 1846.1538
Aquaculture Ponds | 10 |  | 75 |  | 3000 | 225000 | 5 | 55 | 20454.5455
Fences | 30 |  | 27 |  | 6500 | 175500 | 10 | 465 | 3774.1935
Gravel Roads | 10 |  | 2 |  | 10000 | 20000 | 10 | 55 | 3636.3636
Total | [5 empty] | 16710000 |  |  | 693363.6408
¦::
SOUTHERN UNIVERSITY A&M
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 24300 |  | 30 | 59 | 1433700 | 33 | 210 | 225295.7143
Water | 60 | 64500 |  | 4 | 55 | 3547500 | 28 | 1830 | 54278.6885
Fire Mains w/Hydrants | 60 | 3600 |  | 6 | 75 | 270000 | 28 | 1830 | 4131.1475
Fire Hydrants on Domestic Main | 60 |  | 94 |  | 1200 | 112800 | 28 | 1830 | 1725.9016
Sanitary Sewer | 60 | 42800 |  | 8 | 100 | 4280000 | 29 | 1830 | 67825.1366
Storm Sewer | 40 | 16400 |  | 24 | 135 | 2214000 | 28 | 820 | 75600
Gas | 30 | 33500 |  | 3 | 85 | 2847500 | 3 | 465 | 18370.9677
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 73100 |  |  | 90 | 6579000 | 24 | 465 | 339561.2903
Electrical - Overhead | 50 | 8400 |  |  | 6.5 | 54600 | 18 | 1275 | 770.8235
Street Lights - Elec UG | 30 | 38700 |  |  | 45 | 1741500 | 24 | 465 | 89883.871
Street Light Standards | 60 |  | 279 |  | 2000 | 558000 | 24 | 1830 | 7318.0328
Water Wells | 25 |  | 2 |  |  | 400000 | 39 | 325 | 48000
High Mast Light Towers | 50 |  | 7 |  | 18000 | 126000 | 14 | 1275 | 1383.5294
Total | [5 empty] | 24164600 |  |  | 934145.1034
¦::
SOUTHERN UNIVERSITY EXP. FARM
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 3960 |  | 20 | 44 | 174240 | 14 | 210 | 11616
Water | 60 | 9900 |  | 3 | 50 | 495000 | 30 | 1830 | 8114.7541
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0
Fire Hydrants on Domestic Main | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 0 |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 | 1200 |  | 20 | 115 | 138000 | 22 | 820 | 3702.439
Gas | 30 | 0 |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 0 |  |  | 90 | 0 |  | 465 | 0
Electrical - Overhead | 50 | 7000 |  |  | 6.5 | 45500 | 30 | 1275 | 1070.5882
Street Lights - Elec UG | 30 | 0 |  |  | 45 | 0 |  | 465 | 0
Street Light Standards | 60 |  |  |  | 1200 | 0 |  | 1830 | 0
Water Wells | 25 |  | 2 |  | 25000 | 50000 | 30 | 325 | 4615.3846
Sewage Treatment Plants | 20 |  | 4 |  | 3000 | 12000 | 24 | 210 | 1371.4286
Aquaculture Ponds | 10 |  | 4 |  | 25000 | 100000 | 18 | 55 | 32727.2727
Total | [5 empty] | 1014740 |  |  | 63217.8673
¦::
SOUTHERN UNIVERSITY NEW ORLEANS
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 0 |  |  |  | 0 |  | 210 | 0
Water | 60 | 3500 |  | 6 | 60 | 210000 | 22 | 1830 | 2524.5902
Fire Mains w/Hydrants | 60 | 4440 |  | 3 | 65 | 288600 | 22 | 1830 | 3469.5082
Fire Hydrants on Domestic Main | 60 |  |  |  | 1200 | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 2220 |  | 8 | 100 | 222000 | 22 | 1830 | 2668.8525
Storm Sewer | 40 | 3750 |  | 12 | 80 | 300000 | 22 | 820 | 8048.7805
Gas | 30 | 2280 |  | 2.8 | 84 | 191520 | 22 | 465 | 9061.1613
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 2000 |  | 5.5 | 127.5 | 255000 | 16 | 820 | 4975.6098
Chilled Water | 40 | 2000 |  | 5.5 | 170 | 340000 | 16 | 820 | 6634.1463
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 10440 |  |  | 90 | 939600 | 22 | 465 | 44454.1935
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 4000 |  |  | 45 | 180000 | 7 | 465 | 2709.6774
Street Light Standards | 60 |  | 24 |  | 2000 | 48000 | 7 | 1830 | 183.6066
Water Wells | 25 | [6 empty] | 325 | 0
Total | [5 empty] | 2974720 |  |  | 84730.1262
¦::
SOUTHERN UNIVERSITY SHREVEPORT
Concrete Roads & Streets | 40 | 4697 |  | 27 | 77.5 | 364017.5 | 23 | 820 | 10210.247
Asphalt Roads & Streets | 20 | 0 |  |  |  | 0 |  | 210 | 0
Water | 60 | 2100 |  | 4 | 55 | 115500 | 23 | 1830 | 1451.6393
Fire Mains w/Hydrants | 60 | 3766 |  | 8 | 80 | 301280 | 23 | 1830 | 3786.5792
Fire Hydrants on Domestic Main | 60 |  | 0 |  | 1200 | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 5016 |  | 8 | 100 | 501600 | 23 | 1830 | 6304.2623
Storm Sewer | 40 | 4350 |  | 8 | 60 | 261000 | 23 | 820 | 7320.7317
Gas | 30 | 200 |  | 4 | 90 | 18000 | 23 | 465 | 890.3226
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 1850 |  | 10 | 170 | 314500 | 23 | 820 | 8821.3415
Chilled Water | 40 | 1850 |  | 8 | 180 | 333000 | 23 | 820 | 9340.2439
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 2000 |  | 0.25 | 20 | 40000 | 23 | 820 | 1121.9512
Electrical - Underground | 30 | 7666 |  |  | 90 | 689940 | 23 | 465 | 34126.0645
Electrical - Overhead | 50 | 0 |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 5896 |  |  | 45 | 265320 | 23 | 465 | 13123.3548
Street Light Standards | 60 |  | 21 |  | 1200 | 25200 | 23 | 1830 | 316.7213
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Total | [5 empty] | 3229357.5 |  |  | 96813.4594
¦::
LUMCON
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 0 |  |  |  | 0 |  | 210 | 0
Water | 60 | 900 |  | 4 | 55 | 49500 | 4 | 1830 | 108.1967
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0
Fire Hydrants on Domestic Main | 60 |  |  |  | 1200 | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 1500 |  | 6 | 90 | 135000 | 4 | 1830 | 295.082
Storm Sewer | 40 | 950 |  | 10 | 65 | 61750 | 4 | 820 | 301.2195
Gas | 30 | 675 |  | 3 | 85 | 57375 | 4 | 465 | 493.5484
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 675 |  | 4 | 120 | 81000 | 4 | 820 | 395.122
Chilled Water | 40 | 675 |  | 6 | 170 | 114750 | 4 | 820 | 559.7561
Domestic Hot Water | 40 | 675 |  | 4 | 95 | 64125 | 4 | 820 | 312.8049
Compressed Air | 40 | 675 |  | 0.5 | 25 | 16875 | 4 | 820 | 82.3171
Electrical - Underground | 30 | 0 |  |  | 90 | 0 |  | 465 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 3000 |  |  | 45 | 135000 | 4 | 465 | 1161.2903
Street Light Standards | 60 |  | 14 |  | 2000 | 28000 | 4 | 1830 | 61.2022
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Shell Paving | 5 | 195250 |  |  | 0.15 | 29287.5 | 4 | 15 | 7810
Total | [5 empty] | 772662.5 |  |  | 11580.5391
¦::
LSU at ALEXANDRIA
Concrete Roads & Streets | 40 | 0 |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 16711 |  | 28 | 56 | 935816 | 8 | 210 | 35650.1333
Water | 60 | 14550 |  | 6 | 60 | 873000 | 15 | 1830 | 7155.7377
Fire Mains w/Hydrants | 60 | 0 |  |  |  | 0 |  | 1830 | 0
Fire Hydrants on Domestic Main | 60 |  | 13 |  | 1200 | 15600 | 15 | 1830 | 127.8689
Sanitary Sewer | 60 | 15098 |  | 8 | 100 | 1509800 | 25 | 1830 | 20625.6831
Storm Sewer | 40 | 500 |  | 6 | 55 | 27500 | 11 | 820 | 368.9024
Gas | 30 | 10238 |  | 4 | 90 | 921420 | 4 | 465 | 7926.1935
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 4308 |  | 4 | 120 | 516960 | 23 | 820 | 14500.0976
Chilled Water | 40 | 4308 |  | 6 | 170 | 732360 | 23 | 820 | 20541.8049
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 3744 |  | 0.5 | 25 | 93600 | 23 | 820 | 2625.3659
Electrical - Underground | 30 | 5988 |  |  | 90 | 538920 | 10 | 465 | 11589.6774
Electrical - Overhead | 50 | 15347 |  |  | 6.5 | 99755.5 | 30 | 1275 | 2347.1882
Street Lights - Elec UG | 30 | 9800 |  |  | 45 | 441000 | 17 | 465 | 16122.5806
Street Light Standards | 60 |  | 63 |  | 2000 | 126000 | 17 | 1830 | 1170.4918
Water Wells | 25 |  |  |  |  | 15000 | 43 | 325 | 1984.6154
Oxidation Pond | 40 |  | 6 |  | 25000 | 150000 | 30 | 820 | 5487.8049
Water Tower 50,000 gal | 60 |  |  |  |  | 100000 | 43 | 1830 | 2349.7268
Conc. Water Reservoir | 60 |  | 70000 |  |  | 100000 | 43 | 1830 | 2349.7268
Sewage Lift Station | 30 |  |  |  |  | 20000 | 30 | 465 | 1290.3226
Total | [5 empty] | 7216731.5 |  |  | 154213.9217
¦::
LSU A&M
Concrete Roads & Streets | 40 | 11930 |  | 28 | 80 | 954400 | 40 | 820 | 46556.0976
Asphalt Roads & Streets | 20 | 47720 |  | 28 | 56 | 2672320 | 40 | 210 | 509013.3333
Water | 60 | 87660 |  | 6 | 60 | 5259600 | 35 | 1830 | 100593.4426
Fire Mains w/Hydrants | 60 | 44500 |  | 8 | 80 | 3560000 | 17 | 1830 | 33071.0383
Fire Hydrants on Domestic Main | 60
Sanitary Sewer | 60 | 62400 |  | 8 | 100 | 6240000 | 35 | 1830 | 119344.2623
Storm Sewer | 40 | 138700 |  | 10 | 65 | 9015500 | 30 | 820 | 329835.3659
Gas | 30 | 80900 |  | 4 | 90 | 7281000 | 17 | 465 | 266187.0968
Steam & Condensate | 35 | 33800 |  | 6 | 150 | 5070000 | 35 | 630 | 281666.6667
Hot Water | 40 | 7200 |  | 6 | 130 | 936000 | 12 | 820 | 13697.561
Chilled Water | 40 | 25700 |  | 12 | 195 | 5011500 | 23 | 820 | 140566.4634
Domestic Hot Water | 40 | 9000 |  | 2 | 70 | 630000 | 35 | 820 | 26890.2439
Compressed Air | 40 | 5500 |  | 2 | 40 | 220000 | 10 | 820 | 2682.9268
Electrical - Underground | 30 | 158000 |  |  | 90 | 14220000 | 20 | 465 | 611612.9032
Electrical - Overhead | 50 | 5200 |  |  | 6.5 | 33800 | 20 | 1275 | 530.1961
Street Lights - Elec UG | 30 | 95000 |  |  | 45 | 4275000 | 25 | 465 | 229838.7097
Street Light Standards | 60 |  | 475 |  | 2000 | 950000 | 25 | 1830 | 12978.1421
Water Wells | 25 |  |  |  |  | 200000 | 11 | 325 | 6769.2308
Total | [5 empty] | 66529120 |  | 16075 | 2731833.6803
¦::
LSU at EUNICE
Concrete Roads & Streets | 40 | 2150 |  | 20 | 60 | 129000 | 23 | 820 | 3618.2927
Asphalt Roads & Streets | 20 | 5130 |  | 20 | 44 | 225720 | 20 | 210 | 21497.1429
Water | 60 | 7023 |  | 5 | 57.5 | 403822.5 | 23 | 1830 | 5075.3648
Fire Mains w/Hydrants | 60 | 0 |  | 0 |  | 0 | 23 | 1830 | 0
Fire Hydrants on Domestic Main | 60 |  | 3 |  | 1200 | 3600 | 23 | 1830 | 45.2459
Sanitary Sewer | 60 | 4992 |  | 7.8 | 80 | 399360 | 23 | 1830 | 5019.2787
Storm Sewer | 40 | 6430 |  | 22.73 | 135 | 868050 | 23 | 820 | 24347.7439
Gas | 30 | 5275 |  | 1.75 | 80 | 422000 | 23 | 465 | 20873.1183
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 2220 |  | 2.75 | 120 | 266400 | 23 | 820 | 7472.1951
Chilled Water | 40 | 2265 |  | 6.35 | 170 | 385050 | 23 | 820 | 10800.1829
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 2220 |  | 0.75 | 30 | 66600 | 23 | 820 | 1868.0488
Electrical - Underground | 30 | 2660 |  |  | 90 | 239400 | 23 | 465 | 11841.2903
Electrical - Overhead | 50 | 0 |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 5320 |  |  | 45 | 239400 | 23 | 465 | 11841.2903
Street Light Standards | 60 |  | 69 |  | 2000 | 138000 | 23 | 1830 | 1734.4262
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Total | [5 empty] | 3786402.5 |  |  | 126033.6208
¦::
LSU in SHREVEPORT
Concrete Roads & Streets | 40 | 19463 |  | 25 | 77.5 | 1508382.5 | 15 | 820 | 27592.3628
Asphalt Roads & Streets | 20 |  |  |  |  | 0 |  | 210 | 0
Water | 60 | 2555 |  | 4 | 55 | 140525 | 15 | 1830 | 1151.8443
Fire Mains w/Hydrants | 60 | 5750 |  | 8 | 80 | 460000 | 20 | 1830 | 5027.3224
Fire Hydrants on Domestic Main | 60 |  | 7 |  | 1200 | 8400 | 15 | 1830 | 68.8525
Sanitary Sewer | 60 | 4350 |  | 8 | 100 | 435000 | 20 | 1830 | 4754.0984
Storm Sewer | 40 | 9347 |  | 20 | 115 | 1074905 | 15 | 820 | 19662.8963
Gas | 30 | 3443 |  | 4 | 90 | 309870 | 20 | 465 | 13327.7419
Steam & Condensate | 35 | 3241 |  | 8 | 150 | 486150 | 18 | 630 | 13890
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 | 3241 |  | 10 | 185 | 599585 | 18 | 820 | 13161.622
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 3950 |  |  | 90 | 355500 | 15 | 465 | 11467.7419
Electrical - Overhead | 50 |  |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 16530 |  |  | 45 | 743850 | 15 | 465 | 23995.1613
Street Light Standards | 60 |  | 99 |  | 2000 | 198000 | 15 | 1830 | 1622.9508
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Total | [5 empty] | 6320167.5 |  |  | 135722.5946
¦::
LSU MEDICAL CENTER - NEW ORLEANS
Concrete Roads & Streets | 40 | 3925 |  | 30 | 85 | 333625 | 19 | 820 | 7730.3354
Asphalt Roads & Streets | 20 | 400 |  | 30 | 59 | 23600 | 19 | 210 | 2135.2381
Water | 60 | 5700 |  | 6 | 60 | 342000 | 18 | 1830 | 3363.9344
Fire Mains w/Hydrants | 60 | 6490 |  | 8 | 80 | 519200 | 18 | 1830 | 5106.8852
Fire Hydrants on Domestic Main | 60 |  |  |  | 1200 | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 8000 |  | 8 | 100 | 800000 | 18 | 1830 | 7868.8525
Storm Sewer | 40 | 7340 |  | 8 | 60 | 440400 | 18 | 820 | 9667.3171
Gas | 30 | 3930 |  | 4 | 90 | 353700 | 19 | 465 | 14452.2581
Steam & Condensate | 35 | 360 |  | 5 | 150 | 54000 | 19 | 630 | 1628.5714
Hot Water | 40 | 700 |  | 6 | 130 | 91000 | 6 | 820 | 665.8537
Chilled Water | 40 | 1060 |  | 12 | 195 | 206700 | 10 | 820 | 2520.7317
Domestic Hot Water | 40 | 700 |  | 4 | 95 | 66500 | 6 | 820 | 486.5854
Compressed Air | 40 | 1060 |  | 3 | 65 | 68900 | 10 | 820 | 840.2439
Electrical - Underground | 30 | 0 |  |  | 90 | 0 |  | 465 | 0
Electrical - Overhead | 50 | 0 |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 3000 |  |  | 45 | 135000 | 48 | 465 | 13935.4839
Street Light Standards | 60 |  | 0 |  | 2000 | 0 |  | 1830 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Total | [5 empty] | 3434625 |  |  | 70402.2907
¦::
LSU PENNINGTON BIOMEDICAL RESEARCH CENTER
Concrete Roads & Streets | 40 | 3735 |  | 23 | 67.5 | 252112.5 | 5 | 820 | 1537.2713
Asphalt Roads & Streets | 20 | 0 |  |  |  | 0 |  | 210 | 0
Water | 60 | 1850 |  | 8 | 70 | 129500 | 5 | 1830 | 353.8251
Fire Mains w/Hydrants | 60 | 900 |  | 8 | 80 | 72000 | 5 | 1830 | 196.7213
Fire Hydrants on Domestic Main | 60 |  |  |  | 1200 |  |  | 1830 | 0
Sanitary Sewer | 60 | 1390 |  | 8 | 100 | 139000 | 5 | 1830 | 379.7814
Storm Sewer | 40 | 4100 |  | 18 | 110 | 451000 | 5 | 820 | 2750
Gas | 30 | 920 |  | 4 | 90 | 82800 | 5 | 465 | 890.3226
Steam & Condensate | 35 | 0 |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 | 0 |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 0 |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 2235 |  |  | 90 | 201150 | 5 | 465 | 2162.9032
Electrical - Overhead | 50 | 0 |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 5450 |  |  | 45 | 245250 | 5 | 465 | 2637.0968
Street Light Standards | 60 |  | 62 |  | 2000 | 124000 | 5 | 1830 | 338.7978
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Total | [5 empty] | 1696812.5 |  |  | 11246.7196
¦::
LSU MEDICAL CENTER - SHREVEPORT
Concrete Roads & Streets | 40 | 6463 |  | 24 | 70 | 452410 | 20 | 820 | 11034.3902
Asphalt Roads & Streets | 20 | 4542 |  | 24 | 50 | 227100 | 30 | 210 | 32442.8571
Water | 60 | 9331 |  | 8 | 70 | 653170 | 20 | 1830 | 7138.4699
Fire Mains w/Hydrants | 60 | 743 |  | 6 | 75 | 55725 | 30 | 1830 | 913.5246
Fire Hydrants on Domestic Main | 60 |  |  |  | 1200 | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 4516 |  | 8 | 100 | 451600 | 30 | 1830 | 7403.2787
Storm Sewer | 40 | 4780 |  | 10 | 65 | 310700 | 30 | 820 | 11367.0732
Gas | 30 | 1500 |  | 2 | 80 | 120000 | 18 | 465 | 4645.1613
Steam & Condensate | 35 | 4000 |  | 6 | 150 | 600000 | 15 | 630 | 14285.7143
Hot Water | 40 | 700 |  | 3 | 120 | 84000 | 15 | 820 | 1536.5854
Chilled Water | 40 | 2400 |  | 10 | 185 | 444000 | 15 | 820 | 8121.9512
Domestic Hot Water | 40 | 750 |  | 1.5 | 65 | 48750 | 15 | 820 | 891.7683
Compressed Air | 40 | 1000 |  | 0.75 | 30 | 30000 | 10 | 820 | 365.8537
Electrical - Underground | 30 | 6200 |  |  | 90 | 558000 | 18 | 465 | 21600
Electrical - Overhead | 50 | 2640 |  |  | 6.5 | 17160 | 41 | 1275 | 551.8118
Street Lights - Elec UG | 30 | 8650 |  |  | 45 | 389250 | 15 | 465 | 12556.4516
Street Light Standards | 60 |  | 50 |  | 2000 | 100000 | 15 | 1830 | 819.6721
Water Wells | 25 |  |  |  |  | 20000 | 30 | 325 | 1846.1538
Incinerator | 20 |  |  |  |  | 1800000 | 14 | 210 | 120000
Switchgear | 30 |  |  |  |  | 1000000 | 18 | 465 | 38709.6774
Emergency Elec Dist | 30 | 1000 |  | 4 | 50 | 50000 | 10 | 465 | 1075.2688
Medical Gas Bulk Plant | 30 |  | 1 |  |  | 80000 | 10 | 465 | 1720.4301
Medical Gas Piping | 30 | 1100 |  | 1.5 | 40 | 44000 | 10 | 465 | 946.2366
Cooling Tower Piping | 40 | 500 |  | 14 | 200 | 100000 | 15 | 820 | 1829.2683
Total | [5 empty] | 7635865 |  |  | 301801.5984
¦::
UNIVERSITY OF NEW ORLEANS
Concrete Roads & Streets | 40 | 22820 |  | 26 | 80 | 1825600 | 25 | 820 | 55658.5366
Asphalt Roads & Streets | 20 | 1520 |  | 26 | 53 | 80560 | 15 | 210 | 5754.2857
Water | 60 | 28140 |  | 8 | 70 | 1969800 | 25 | 1830 | 26909.8361
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Hydrants on Domestic Main | 60 |  | 54 |  | 1200 | 64800 | 20 | 1830 | 708.1967
Sanitary Sewer | 60 | 22930 |  | 10 | 120 | 2751600 | 25 | 1830 | 37590.1639
Storm Sewer | 40 | 42540 |  | 24 | 135 | 5742900 | 25 | 820 | 175088.4146
Gas | 30 | 10860 |  | 4 | 90 | 977400 | 25 | 465 | 52548.3871
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 | 9916 |  | 5 | 125 | 1239500 | 25 | 820 | 37789.6341
Chilled Water | 40 | 11076 |  | 12 | 195 | 2159820 | 25 | 820 | 65848.1707
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 | 9916 |  | 2 | 40 | 396640 | 25 | 820 | 12092.6829
Electrical - Underground | 30 | 28040 |  |  | 90 | 2523600 | 10 | 465 | 54270.9677
Electrical - Overhead | 50 |  |  |  | 6.5 | 0 |  | 1275 | 0
Street Lights - Elec UG | 30 | 6000 |  |  | 45 | 270000 | 1 | 465 | 580.6452
Street Light Standards | 60 |  | 96 |  | 2000 | 192000 | 16 | 1830 | 1678.6885
Water Wells | 25 |  | 4 |  |  | 1160000 | 19 | 325 | 67815.3846
Condensor Water Well | 25 | 3620 |  | 12 | 65 | 235300 | 25 | 325 | 18100
480V Emergency Power | 30 | 11456 |  |  | 25 | 286400 | 20 | 465 | 12318.2796
High Mast Light Towers | 50 |  | 15 |  | 42000 | 630000 | 3 | 1275 | 1482.3529
Total | [5 empty] | 22505920 |  |  | 626234.6271
¦::
BURDEN RESEARCH PLANTATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 5280 |  | 20 | 44 | 232320 | 7 | 210 | 7744
Water | 60 | 6000 |  | 6 | 60 | 360000 | 15 | 1830 | 2950.8197
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 95000 | 23 | 325 | 6723.0769
Fences | 30 |  | 6.8 |  | 6500 | 44200 | 22 | 465 | 2091.1828
Sewage Treatment Plants | 20 |  | 6 |  | 3000 | 18000 | 16 | 210 | 1371.4286
Gravel Roads | 10 |  | 6.5 |  | 10000 | 65000 | 12 | 55 | 14181.8182
Drainage Structures | 20 |  |  |  |  | 15000 | 20 | 210 | 1428.5714
Total | [5 empty] | 829520 |  |  | 36490.8976
¦::
CENTRAL STATIONS
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 600 |  | 20 | 44 | 26400 | 16 | 210 | 2011.4286
Water | 60 | 15000 |  | 4 | 55 | 825000 | 18 | 1830 | 8114.7541
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 | 3500 |  | 1.5 | 75 | 262500 | 40 | 465 | 22580.6452
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 | 10000 |  |  | 90 | 900000 | 25 | 1275 | 17647.0588
Water Wells | 25 |  |  |  |  | 265000 | 25 | 325 | 20384.6154
Fences | 30 |  | 16.8 |  | 6500 | 109200 | 18 | 465 | 4227.0968
Sewage Treatment Plants | 20 |  | 18 |  | 3000 | 54000 | 21 | 210 | 5400
Gravel Roads | 10 |  | 18.6154 |  | 6500 | 121000 | 12 | 55 | 26400
Drainage Structures | 20 |  |  |  |  | 500000 | 12 | 210 | 28571.4286
Total | [5 empty] | 3063100 |  |  | 135337.0274
¦::
DEAN LEE RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 |  |  |  |  | 0 |  | 210 | 0
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Fences | 30 |  | 27 |  | 6500 | 175500 | 20 | 465 | 7548.3871
Sewage Treatment Plants | 20 |  | 16 |  | 3000 | 48000 | 15 | 210 | 3428.5714
Gravel Roads | 10 |  | 3.9 |  | 10000 | 39000 | 15 | 55 | 10636.3636
Drainage Structures | 20 |  |  |  |  | 350000 | 25 | 210 | 41666.6667
Total | [5 empty] | 612500 |  |  | 63279.9888
¦::
HAMMOND RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 1056 |  | 20 | 44 | 46464 | 11 | 210 | 2433.8286
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 60000 | 18 | 325 | 3323.0769
Fences | 30 |  | 3 |  | 6500 | 19500 | 15 | 465 | 629.0323
Sewage Treatment Plants | 20 |  | 12 |  | 3000 | 36000 | 18 | 210 | 3085.7143
Gravel Roads | 10 |  | 0.2 |  | 10000 | 2000 | 15 | 55 | 545.4545
Drainage Structures | 20 |  |  |  |  | 50000 | 15 | 210 | 3571.4286
Total | [5 empty] | 213964 |  |  | 13588.5352
¦::
IBERIA RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 2640 |  | 20 | 44 | 116160 | 8 | 210 | 4425.1429
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Fences | 30 |  | 18.1 |  | 6500 | 117650 | 15 | 465 | 3795.1613
Sewage Treatment Plants | 20 |  | 10 |  | 3000 | 30000 | 12 | 210 | 1714.2857
Gravel Roads | 10 |  | 7.5 |  | 10000 | 75000 | 10 | 55 | 13636.3636
Drainage Structures | 20 |  |  |  |  | 200000 | 20 | 210 | 19047.619
Total | [5 empty] | 538810 |  |  | 42618.5725
¦::
IDLEWILD RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 |  |  |  |  | 0 |  | 210 | 0
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 120000 | 15 | 325 | 5538.4615
Fences | 30 |  | 24.5 |  | 6500 | 159250 | 12 | 465 | 4109.6774
Sewage Treatment Plants | 20 |  | 7 |  | 3000 | 21000 | 10 | 210 | 1000
Gravel Roads | 10 |  | 11.6 |  | 10000 | 116000 | 15 | 55 | 31636.3636
Drainage Structures | 20 |  |  |  |  | 90000 | 10 | 210 | 4285.7143
Total | [5 empty] | 506250 |  |  | 46570.2169
¦::
CALHOUN RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 6336 |  | 18 | 41 | 259776 | 8 | 210 | 9896.2286
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 25000 | 13 | 325 | 1000
Fences | 30 |  | 11.7 |  | 6500 | 76050 | 18 | 465 | 2943.871
Sewage Treatment Plants | 20 |  | 11 |  | 3000 | 33000 | 15 | 210 | 2357.1429
Gravel Roads | 10 |  | 0.1 |  | 10000 | 1000 | 10 | 55 | 181.8182
Drainage Structures | 20 |  |  |  |  | 50000 | 18 | 210 | 4285.7143
Total | [5 empty] | 444826 |  |  | 20664.7749
¦::
HILL FARM RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 50160 |  | 18 | 41 | 2056560 | 10 | 210 | 97931.4286
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Fences | 30 |  | 56 |  | 6500 | 364000 | 25 | 465 | 19569.8925
Sewage Treatment Plants | 20 |  | 18 |  | 3000 | 54000 | 15 | 210 | 3857.1429
Gravel Roads | 10 |  | 2 |  | 10000 | 20000 | 10 | 55 | 3636.3636
Drainage Structures | 20 |  |  |  |  | 50000 | 20 | 210 | 4761.9048
Total | [5 empty] | 2544560 |  |  | 129756.7323
¦::
NORTHEAST RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 5808 |  | 12 | 32 | 185856 | 10 | 210 | 8850.2857
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 125000 | 9 | 325 | 3461.5385
Fences | 30 |  | 56 |  | 6500 | 364000 | 12 | 465 | 9393.5484
Sewage Treatment Plants | 20 |  | 10 |  | 3000 | 30000 | 13 | 210 | 1857.1429
Gravel Roads | 10 |  | 6.4 |  | 10000 | 64000 | 15 | 55 | 17454.5455
Drainage Structures | 20 |  |  |  |  | 150000 | 15 | 210 | 10714.2857
Total | [5 empty] | 918856 |  |  | 51731.3466
¦::
PECAN RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 2112 |  | 15 | 36.5 | 77088 | 10 | 210 | 3670.8571
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 25000 | 16 | 325 | 1230.7692
Fences | 30 |  | 0.9 |  | 6500 | 5850 | 9 | 465 | 113.2258
Sewage Treatment Plants | 20 |  | 3 |  | 3000 | 9000 | 12 | 210 | 514.2857
Gravel Roads | 10 |  | 1.2 |  | 10000 | 12000 | 8 | 55 | 1745.4545
Drainage Structures | 20 |  |  |  |  | 25000 | 10 | 210 | 1190.4762
Total | [5 empty] | 153938 |  |  | 8465.0686
¦::
CITRUS RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 1056 |  | 20 | 44 | 46464 | 7 | 210 | 1548.8
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Fences | 30 |  | 2 |  | 6500 | 13000 | 15 | 465 | 419.3548
Sewage Treatment Plants | 20 |  | 8 |  | 3000 | 24000 | 12 | 210 | 1371.4286
Gravel Roads | 10 |  | 3 |  | 1000 | 3000 | 10 | 55 | 545.4545
Drainage Structures | 20 |  |  |  |  | 150000 | 9 | 210 | 6428.5714
Total | [5 empty] | 236464 |  |  | 10313.6094
¦::
RED RIVER RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 4752 |  | 20 | 44 | 209088 | 12 | 210 | 11947.8857
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 110000 | 20 | 325 | 6769.2308
Fences | 30 |  | 11.5 |  | 6500 | 74750 | 10 | 465 | 1607.5269
Sewage Treatment Plants | 20 |  | 10 |  | 3000 | 30000 | 18 | 210 | 2571.4286
Gravel Roads | 10 |  | 0.6 |  | 10000 | 6000 | 14 | 55 | 1527.2727
Drainage Structures | 20 |  |  |  |  | 90000 | 10 | 210 | 4285.7143
Total | [5 empty] | 519838 |  |  | 28709.0589
¦::
RICE RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 528 |  | 20 | 44 | 23232 | 9 | 210 | 995.6571
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  | 10 |  | 23350 | 233500 | 35 | 325 | 25146.1538
Fences | 30 |  | 19.5 |  | 6500 | 126750 | 18 | 465 | 4906.4516
Sewage Treatment Plants | 20 |  | 15 |  | 3000 | 45000 | 16 | 210 | 3428.5714
Gravel Roads | 10 |  | 5.6 |  | 10000 | 56000 | 9 | 55 | 9163.6364
Drainage Structures | 20 |  |  |  |  | 250000 | 10 | 210 | 11904.7619
Irrigation Sys UG Piping | 30 |  |  |  |  | 341000 | 15 | 465 | 11000
Total | [5 empty] | 1075482 |  |  | 66545.2323
¦::
ST. GABRIEL RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 1056 |  | 18 | 41 | 43296 | 8 | 210 | 1649.3714
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 5000 |  | 4 | 85 | 425000 | 20 | 1830 | 4644.8087
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 | 4000 |  | 1.5 | 75 | 300000 | 20 | 465 | 12903.2258
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 65000 | 25 | 325 | 5000
Fences | 30 |  | 22.3 |  | 6500 | 144950 | 21 | 465 | 6546.129
Sewage Treatment Plants | 20 |  | 21.6667 |  | 3000 | 65000 | 10 | 210 | 3095.2381
Gravel Roads | 10 |  | 5.7 |  | 10000 | 57000 | 15 | 55 | 15545.4545
Drainage Structures | 20 |  |  |  |  | 300000 | 20 | 210 | 28571.4286
Total | [5 empty] | 1400246 |  |  | 77955.6562
¦::
SOUTHEAST RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 16896 |  | 20 | 44 | 743424 | 15 | 210 | 53101.7143
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Fences | 30 |  | 40 |  | 6500 | 260000 | 16 | 465 | 8946.2366
Sewage Treatment Plants | 20 |  | 11 |  | 3000 | 33000 | 14 | 210 | 2200
Gravel Roads | 10 |  | 4.2 |  | 10000 | 42000 | 15 | 55 | 11454.5455
Drainage Structures | 20 |  |  |  |  | 50000 | 15 | 210 | 3571.4286
Total | [5 empty] | 1128424 |  |  | 79273.9249
¦::
SWEET POTATO RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 158.4 |  | 20 | 44 | 6969.6 | 9 | 210 | 298.6971
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Fences | 30 |  | 1.8 |  | 6500 | 11700 | 22 | 465 | 553.5484
Sewage Treatment Plants | 20 |  | 6 |  | 3000 | 18000 | 26 | 210 | 2228.5714
Gravel Roads | 10 |  | 1.7 |  | 10000 | 17000 | 9 | 55 | 2781.8182
Drainage Structures | 20 |  |  |  |  | 50000 | 13 | 210 | 3095.2381
Total | [5 empty] | 103669.6 |  |  | 8957.8732
¦::
ROSEPINE RESEARCH STATION
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 | 3168 |  | 15 | 36.5 | 115632 | 12 | 210 | 6607.5429
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 0 |  | 325 | 0
Fences | 30 |  | 11.5 |  | 6500 | 74750 | 8 | 465 | 1286.0215
Sewage Treatment Plants | 20 |  | 8 |  | 3000 | 24000 | 23 | 210 | 2628.5714
Gravel Roads | 10 |  | 2.3 |  | 10000 | 23000 | 15 | 55 | 6272.7273
Drainage Structures | 20 |  |  |  |  | 50000 | 8 | 210 | 1904.7619
Total | [5 empty] | 287382 |  |  | 18699.625
¦::
LEE MEMORIAL FOREST
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 |  |  |  |  | 0 |  | 210 | 0
Water | 60 |  |  |  |  | 0 |  | 1830 | 0
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 |  |  |  |  | 0 |  | 1830 | 0
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Overhead | 50 |  |  |  |  | 0 |  | 1275 | 0
Water Wells | 25 |  |  |  |  | 5000 | 13 | 325 | 200
Fences | 30 |  | 3.9 |  | 6500 | 25350 | 10 | 465 | 545.1613
Sewage Treatment Plants | 20 |  | 4 |  | 3000 | 12000 | 15 | 210 | 857.1429
Gravel Roads | 10 |  | 3 |  | 10000 | 30000 | 10 | 55 | 5454.5455
Drainage Structures | 20 |  |  |  |  | 25000 | 10 | 210 | 1190.4762
Total | [5 empty] | 97350 |  |  | 8247.3258
¦::
CAMP GRANT WALKER
Concrete Roads & Streets | 40 |  |  |  |  | 0 |  | 820 | 0
Asphalt Roads & Streets | 20 |  |  |  |  | 0 |  | 210 | 0
Water | 60 | 4300 |  | 2 | 45 | 193500 | 5 | 1830 | 528.6885
Fire Mains w/Hydrants | 60 |  |  |  |  | 0 |  | 1830 | 0
Sanitary Sewer | 60 | 3350 |  | 4 | 85 | 284750 | 5 | 1830 | 778.0055
Storm Sewer | 40 |  |  |  |  | 0 |  | 820 | 0
Gas | 30 |  |  |  |  | 0 |  | 465 | 0
Steam & Condensate | 35 |  |  |  |  | 0 |  | 630 | 0
Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Chilled Water | 40 |  |  |  |  | 0 |  | 820 | 0
Domestic Hot Water | 40 |  |  |  |  | 0 |  | 820 | 0
Compressed Air | 40 |  |  |  |  | 0 |  | 820 | 0
Electrical - Underground | 30 | 2200 |  |  | 90 | 198000 | 5 | 465 | 2129.0323
Water Wells | 25 |  |  |  |  | 15000 | 15 | 325 | 692.3077
Fences | 30 |  | 3.8462 |  | 6500 | 25000 | 8 | 465 | 430.1075
Sewage Treatment Plants | 20 |  | 1 |  | 75000 | 75000 | 9 | 210 | 3214.2857
Gravel Roads | 10 |  | 0.6 |  | 10000 | 6000 | 7 | 55 | 763.6364
Drainage Structures | 20 |  |  |  |  | 50000 | 8 | 210 | 1904.7619
Total | [5 empty] | 847250 |  |  | 10440.8254
¦::
LSU AGRICULTURAL CENTER
SUMMARY OF RESEARCH STATIONS
BURDEN | [5 empty] | 829520 |  |  | 36490.8976
CENTRAL STATIONS | [5 empty] | 3063100 |  |  | 135337.0274
DEAN LEE | [5 empty] | 612500 |  |  | 63279.9888
HAMMOND | [5 empty] | 213964 |  |  | 13588.5352
IBERIA | [5 empty] | 538810 |  |  | 42618.5725
IDELWILD | [5 empty] | 506250 |  |  | 46570.2169
CALHOUN | [5 empty] | 444826 |  |  | 20664.7749
HILL FARM | [5 empty] | 2544560 |  |  | 129756.7323
NORTHEAST | [5 empty] | 918856 |  |  | 51731.3466
PECAN | [5 empty] | 153938 |  |  | 8465.0686
CITRUS | [5 empty] | 236464 |  |  | 10313.6094
RED RIVER | [5 empty] | 519838 |  |  | 28709.0589
RICE | [5 empty] | 1075482 |  |  | 66545.2323
ST. GABRIEL | [5 empty] | 1400246 |  |  | 77955.6562
SOUTHEAST | [5 empty] | 1128424 |  |  | 79273.9249
SWEET POTATO | [5 empty] | 103669.6 |  |  | 8957.8732
ROSEPINE | [5 empty] | 287382 |  |  | 18699.625
LEE MEMORIAL FOREST | [5 empty] | 97350 |  |  | 8247.3258
CAMP GRANT WALKER | [5 empty] | 847250 |  |  | 10440.8254
TOTAL | [5 empty] | 15522429.6 |  |  | 857646.2919
¦::
SUMMARY OF UTILITY SYSTEM RENEWAL ALLOWANCES
DELGADO | [5 empty] | 3629505 |  |  | 124162.5474
GRAMBLING | [5 empty] | 12868316.5 |  |  | 364632.2864
LOUISIANA TECH | [5 empty] | 16161830 |  |  | 674434.1346
MC NEESE | [5 empty] | 11362685 |  |  | 364401.7632
NICHOLLS | [5 empty] | 2132000 |  |  | 77310.7705
NORTHEAST | [5 empty] | 12696572.5 |  |  | 384430.5466
NORTHWESTERN | [5 empty] | 22684820 |  |  | 472528.2726
SOUTHEASTERN | [5 empty] | 16093535 |  |  | 613027.0112
USL | [5 empty] | 16710000 |  |  | 693363.6408
SOUTHERN A&M | [5 empty] | 25179340 |  |  | 997362.9706
SOUTHERN NO | [5 empty] | 2974720 |  |  | 84730.1262
SOUTHERN S | [5 empty] | 3229357.5 |  |  | 96813.4594
LUMCON | [5 empty] | 772662.5 |  |  | 11580.5391
LSU A | [5 empty] | 7216731.5 |  |  | 154213.9217
LSU A&M | [5 empty] | 66529120 |  |  | 2731833.6803
LSU AG CENTER | [5 empty] | 15522429.6 |  |  | 857646.2919
LSU E | [5 empty] | 3786402.5 |  |  | 126033.6208
LSU S | [5 empty] | 6320167.5 |  |  | 135722.5946
LSUMC NO | [5 empty] | 3434625 |  |  | 70402.2907
LSUMC P | [5 empty] | 1696812.5 |  |  | 11246.7196
LSUMC S | [5 empty] | 7635865 |  |  | 301801.5984
UNO | [5 empty] | 22505920 |  |  | 626234.6271
TOTAL | [5 empty] | 281143417.6 |  |  | 9973913.4136